[image: image1.jpg]LEYU
=



               浙江乐宇电气有限公司
Zhejiang Leyu Electric Co., Ltd   

240W Single Output Industrial Din Rail Power Supply                     WDR-240 series
[image: image2.png]


Features:

ingle and two phase wide input range 180~550VAC

Built-in active PFC circuit compliance to EN61000-3-2

High efficiency 91% and low power dissipation

Protections: Short circuit / Overload / Over voltage / Over temperature

Cooling by free air convection

Can be installed on DIN rail TS-35/7.5 or 15

UL 508(industrial control equipment)approved

EN61000-6-2/EN50082-2) industrial immunity level

Built-in DC OK relay contact

100% full load burn-in test

2 years warranty

SPECIFICATION

	MODEL
	WDR-240-24
	WDR-240-48

	OUTPUT
	DC VOLTAGE
	24V
	48V

	
	RATED CURRENT
	10A
	5A

	
	CURRENT RANGE
	0 ~ 10A
	0 ~ 5A

	
	RATED POWER
	240W
	240W

	
	RIPPLE & NOISE (max.)
	150mVp-p
	150mVp-p

	
	VOLTAGE ADJ. RANGE
	24 ~ 28V
	48 ~ 55V

	
	VOLTAGE TOLERANCE
	±1.0%
	±1.0%

	
	LINE REGULATION
	±0.5%
	±0.5%

	
	LOAD REGULATION
	±1.0%
	±1.0%

	
	SETUP, RISE TIME
	800ms, 150ms/400VAC 1500ms, 150ms/230VAC at full load

	
	HOLD UP TIME (Typ.)
	18ms / 400VAC 18ms / 230VAC at full load

	INPUT
	VOLTAGE RANGE
	180 ~ 550VAC 254 ~ 780VDC

	
	FREQUENCY RANGE
	47 ~ 63Hz

	
	POWER FACTOR (Typ.)
	PF≥0.84/400VAC PF≥0.84/230VAC

	
	EFFICIENCY (Typ.)
	91%

	
	AC CURRENT (Typ.)
	1A/400VAC 2A/230VAC

	
	INRUSH CURRENT (Typ.)
	COLD START 50A

	
	LEAKAGE CURRENT
	<3.5mA / 530VAC

	PROTECTION
	OVERLOAD
	105 ~ 130% rated output power

	
	
	Protection type: Constant current limiting, unit will shut down after 3 sec., auto-recovery after 1 minute if the fault condition is removed

	
	OVER VOLTAGE
	29 ~ 33V
	56 ~ 65V

	
	
	Protection type: Shut down o/p voltage, auto-recovery after 1 minute if the fault condition is removed

	
	OVER TEMPERATURE
	90°C ±5°C (TSW) detect on heatsink of power switch

	
	
	Protection type: Shut down o/p voltage, recovers automatically after temperature goes down

	FUNCTION
	DC OK REALY CONTACT RATINGS (max.)
	60Vdc/0.3A, 30Vdc/1A, 30Vac/0.5A resistive load

	ENVIRONMENT
	WORKING TEMP.
	-30 ~ +70°C (Refer to "Derating Curve")

	
	WORKING HUMIDITY
	20 ~ 95% RH non-condensing

	
	STORAGE TEMP., HUMIDITY
	-40 ~ +85°C, 10 ~ 95% RH

	
	TEMP. COEFFICIENT
	±0.03%/°C (0 ~ 50°C)

	
	VIBRATION
	Component: 10 ~ 500Hz, 2G 10min./1cycle, 60min. each along X, Y, Z axes; Mounting: Compliance to IEC60068-2-6

	SAFETY & EMC
	SAFETY STANDARDS
	UL508, AS/NZS 62368.1, EAC TP TC 004 approved, IEC62368-1 CB approved by SIQ, design refer to GL;(meet EN60204-1)

	
	WITHSTAND VOLTAGE
	I/P-O/P-3KVAC I/P-FG:2KVAC O/P-FG:0.5KVAC O/P-DC OK:0.5KVAC

	
	ISOLATION RESISTANCE
	I/P-O/P, I/P-FG, O/P-FG:>100M Ohms / 500VDC / 25°C/ 70% RH

	
	EMC EMISSION
	Compliance to EN55032 (CISPR32), EN61204-3 Class B, EN61000-3-2,-3, EAC TP TC 020

	
	EMC IMMUNITY
	Compliance to EN61000-4-2,3,4,5,6,8,11, EN55024, EN61000-6-2 (EN50082-2), EN61204-3, heavy industry level, criteria A, EAC TP TC 020 approved

	OTHERS
	MTBF
	141.1K hrs min. MIL-HDBK-217F (25°C)

	
	DIMENSION
	63*125.2*113.5mm (W*H*D)

	
	PACKING
	1.06Kg; 12pcs/13.7Kg/1.22CUFT

	NOTE
	1. All parameters NOT specially mentioned are measured at 400VAC input, rated load and 25°C of ambient temperature. 
2. Ripple & noise are measured at 20MHz of bandwidth by using a 12" twisted pair-wire terminated with a 0.1uf & 47uf parallel capacitor. 
3. Tolerance : includes set up tolerance, line regulation and load regulation. 
4. The power supply is considered a component which will be installed into a final equipment. The final equipment must be re-confirmed that it still meets EMC directives. 
5. Installation clearances : 40mm on top, 20mm on the bottom, 5mm on the left and right side are recommended when loaded permanently with full power. In case the adjacent device is a heat source, 15mm clearance is recommended. 
6. Derating may be needed under low input voltage. Please check the derating curve for more details. 
7. The ambient temperature derating of 3.5°C/1000m with fanless models and of 5°C/1000m with fan models for operating altitude higher than 2000m(6500ft).


Website：http://www.leyuelec.com      http://www.zjlyn.com        E-mail：Leyu@leyuelec.com TEL:0086(577)62998958/62998960   FAX:0086(577)62998961    Mob/whatsapp: +8618906669219

